## Dashboard
AI Factory Dashboard — 32x Vera Rubin NVL72, Abu Dhabi
Headline KPIs, all live-linked; edit assumptions on 'Control Panel & Inputs'
KPI | Value | Unit | Source Sheet
Equity IRR (5-Yr, levered) | 126.5% | % | 5Yr Pro Forma Financials
Project IRR (5-Yr, unlevered) | 37.55% | % | 5Yr Pro Forma Financials
Equity NPV @ hurdle rate | 109809242.3148 | USD | 5Yr Pro Forma Financials
MOIC | 7.6253 | x | 5Yr Pro Forma Financials
Payback Period | 0.88301 | years | 5Yr Pro Forma Financials
Year 1 Gross Revenue | 75600000 | USD | 5Yr Pro Forma Financials
Year 1 EBITDA | 60755550.3219 | USD | 5Yr Pro Forma Financials
Year 1 EBITDA Margin | 80.36% | % | 5Yr Pro Forma Financials
Minimum DSCR | 2.2624 | x | 5Yr Pro Forma Financials
Peak MLC vs ASHRAE 90.4 | 0.077832 | (limit 0.260) | Thermal Hydraulics & MLC
MLC Compliance Margin | 70.06% | % | Thermal Hydraulics & MLC
Annual Facility Energy | 66124.1613 | MWh/yr | Thermal Hydraulics & MLC
Annual Carbon Emissions | 25788.4229 | tCO2/yr | Thermal Hydraulics & MLC
Annual Water Consumption | 9918.6242 | m³/yr | Thermal Hydraulics & MLC
Total GPU Count | 2304 | GPUs | Unit Economics & KPIs
CapEx per GPU | 60546.875 | $/GPU | Unit Economics & KPIs
Blended Revenue per Sold GPU-hour | 5.0132 | $/GPU-hr | Unit Economics & KPIs
Cash Cost per M Tokens | 0.13787 | $/M tok | Unit Economics & KPIs
Energy Cost as % of Revenue | 4.729% | % | Unit Economics & KPIs
Breakeven Power Tariff | 1.1247 | $/kWh | Unit Economics & KPIs

## Control Panel & Inputs
NVIDIA Vera Rubin NVL72 AI Factory — Abu Dhabi
Master Control Panel — edit only the yellow Value cells; every other sheet recalculates from them
Category | Parameter | Value | Unit | Notes / Constraints
Geographic & Climate | Geo_Location | Abu Dhabi, UAE |  | ASHRAE Climate Zone 1A
Geographic & Climate | Peak_Ambient_DryBulb | 50 | °C | Extreme peak dry-bulb temperature
Geographic & Climate | Coincident_WetBulb | 30 | °C | Peak summer wet-bulb condition
Geographic & Climate | Grid_Carbon_Intensity | 0.39 | kgCO2/kWh | Assumption: Abu Dhabi grid avg (Barakah nuclear + gas + solar mix)
Geographic & Climate | Water_Usage_Effectiveness | 0.15 | L/kWh | Assumption: closed-loop dry coolers, minimal adiabatic assist
Technical Specs | Rack_Count | 32 | racks | Vera Rubin NVL72 racks
Technical Specs | GPUs_Per_Rack | 72 | GPUs | NVL72 = 72 Rubin GPUs per rack
Technical Specs | Peak_Power_Per_Rack | 227 | kW | Compute & scale-up busbar load
Technical Specs | Air_Cooled_Load | 1000 | kW | 1.0 MW network & NVMe storage
Technical Specs | Liquid_Supply_Temp_FWS | 45 | °C | S45 direct-to-chip loop
Technical Specs | Target_Annualized_PUE | 1.08 |  | Drives facility energy = IT energy x PUE
Technical Specs | Cluster_Utilization | 85% | % | Assumption: avg power/capacity utilization of the fleet
Technical Specs | Uptime_Availability | 99.5% | % | Assumption: contractual availability SLA
Technical Specs | Tokens_Per_GPU_Sec | 1800 | tok/s/GPU | Assumption: blended inference throughput per Rubin GPU
Technical Specs | Token_Fleet_Share | 30% | % | Share of fleet serving the API token market
Financial & Fiscal | Electricity_Tariff | 0.06 | $/kWh | Abu Dhabi industrial rate (Year 1)
Financial & Fiscal | Tariff_Escalation | 2% | %/yr | Assumption: annual power price escalation
Financial & Fiscal | CapEx_Initial | 139500000 | USD | Total turnkey deployment
Financial & Fiscal | Residual_Value_Pct | 10% | % | Assumption: pre-tax residual recovery of CapEx at end of Year 5
Financial & Fiscal | Debt_Ratio | 80% | % | User adjustable (50% - 80%)
Financial & Fiscal | Interest_Rate | 6.5% | % | Senior debt facility rate
Financial & Fiscal | Debt_Tenor | 5 | Years | Annual amortization schedule
Financial & Fiscal | UAE_Corporate_Tax | 9% | % | Statutory corporate tax rate
Financial & Fiscal | GIDLR_EBITDA_Cap | 30% | % | UAE interest deduction limit — applied via MIN() in the tax calc
Financial & Fiscal | Equity_Discount_Rate | 15% | % | Assumption: hurdle rate for equity NPV
Financial & Fiscal | Fixed_OpEx_Annual | 10877000 | USD/yr | Staff, maintenance, insurance, connectivity (Year 1)
Financial & Fiscal | OpEx_Escalation | 3% | %/yr | Assumption: annual fixed-OpEx inflation
Revenue Strategy | Lease_Revenue_70pct | 58800000 | USD/yr | 70% bare-metal capacity leases (Year 1, pre-ramp)
Revenue Strategy | Token_Revenue_30pct | 25200000 | USD/yr | 30% dynamic API token market (Year 1, pre-ramp)
Revenue Strategy | Year1_Ramp_Factor | 90% | % | Assumption: Year 1 commissioning / fill-up ramp
Revenue Strategy | Lease_Price_Escalation | 0% | %/yr | Assumption: lease repricing per year
Revenue Strategy | Token_Price_Decline | 15% | %/yr | Core tokenomics: $/token deflation per year
Revenue Strategy | Token_Volume_Growth | 25% | %/yr | Token demand growth (partially offsets price decline)
Legend: yellow cells with blue text are the editable inputs; all other cells in this workbook are formulas.
Rows marked 'Assumption' are user-supplied estimates, not sourced market data — revisit before investment use.

## Thermal Hydraulics & MLC
Thermal Hydraulics & ASHRAE 90.4 Compliance Engine
S45 closed-loop fluid dynamics, 3-stage trim cooling, and annual energy / water / carbon footprint
Metric / Calculation Step | Value | Unit | Notes
Compute IT Load | 7264 | kW | Racks x kW/rack
Network & Storage Air Load | 1000 | kW | Continuous air-cooled load
Total Combined IT Load | 8264 | kW | Compute + network/storage
S45 Loop Supply Temperature | 45 | °C | Facility Water Supply (FWS)
S45 Loop Return Temperature | 55 | °C | Facility Water Return (FWR) — assumption
S45 Loop Delta T | 10 | °C | Hydraulic temperature split
S45 Liquid Flow Rate per Rack | 195 | LPM | PG25 water/glycol mixture — vendor spec
Total S45 Cluster Flow Rate | 6240 | LPM | Primary CDU manifold demand
Peak Ambient Dry-Bulb | 50 | °C | Abu Dhabi extreme condition
S45 Peak Rejection Approach | 5 | K | FWR minus peak dry-bulb (positive = dry cooling viable)
S45 Dry Cooler / CDU Cooling Power | 363.2 | kW | 5% of liquid-cooled load — CDU pumps & EC fans (assumption)
Air Loop Chiller Cooling Power | 280 | kW | 28% of air-cooled load — high-ambient screw chillers (assumption)
Total Cooling Peak Power | 643.2 | kW | Combined cooling power
Peak Mechanical Load Component (MLC) | 0.077832 |  | Cooling power / total IT load
ASHRAE 90.4 Zone 1A Limit | 0.26 |  | Maximum allowable peak MLC threshold
Safety Compliance Margin | 70.06% | % | Operational margin under the Zone 1A limit
Average Utilized IT Power | 6989.278 | kW | Total IT x utilization x uptime
Annualized PUE | 1.08 |  | Facility energy multiplier on IT energy
Annual Facility Energy | 66124.1613 | MWh/yr | Avg IT power x 8760h x PUE
Annual Water Consumption | 9918.6242 | m³/yr | Facility kWh x WUE
Annual Carbon Emissions | 25788.4229 | tCO2/yr | Facility kWh x grid intensity

## 5Yr Pro Forma Financials
5-Year Leveraged Financial Model & Debt Amortization
UAE corporate tax (9%) with GIDLR 30%-of-EBITDA interest cap, revenue ramp & escalations, full debt schedule and equity returns
Line Item (USD) | Year 0 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5
Revenue Ramp Factor | 0% | 90% | 100% | 100% | 100% | 100%
Lease Revenue | 0 | 52920000 | 58800000 | 58800000 | 58800000 | 58800000
Token Revenue | 0 | 22680000 | 26775000 | 28448437.5 | 30226464.8438 | 32115618.8965
Gross Annual Revenue | 0 | 75600000 | 85575000 | 87248437.5 | 89026464.8438 | 90915618.8965
Effective Power Tariff | 0 | 0.06 | 0.0612 | 0.062424 | 0.063672 | 0.064946
Annual Facility Energy (kWh) | 0 | 66124161.3024 | 66124161.3024 | 66124161.3024 | 66124161.3024 | 66124161.3024
Electricity Cost | 0 | 3967449.6781 | 4046798.6717 | 4127734.6451 | 4210289.338 | 4294495.1248
Fixed Non-Power OpEx | 0 | 10877000 | 11203310 | 11539409.3 | 11885591.579 | 12242159.3264
Total Operational Expense (OpEx) | 0 | 14844449.6781 | 15250108.6717 | 15667143.9451 | 16095880.917 | 16536654.4512
EBITDA | 0 | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
EBITDA Margin | 0% | 80.36% | 82.18% | 82.04% | 81.92% | 81.81%
CapEx Initial Outlay | 139500000 | 0 | 0 | 0 | 0 | 0
Debt Financed Amount | 111600000 | 0 | 0 | 0 | 0 | 0
Equity Outlay | 27900000 | 0 | 0 | 0 | 0 | 0
Beginning Debt Balance | 0 | 111600000 | 91999185.6041 | 71124318.2725 | 48892584.5643 | 25215788.1651
Annual Debt Service (P+I) | 0 | 26854814.3959 | 26854814.3959 | 26854814.3959 | 26854814.3959 | 26854814.3959
Interest Expense | 0 | 7254000 | 5979947.0643 | 4623080.6877 | 3178017.9967 | 1639026.2307
Debt Principal Payment | 0 | 19600814.3959 | 20874867.3316 | 22231733.7082 | 23676796.3992 | 25215788.1651
Ending Debt Balance | 0 | 91999185.6041 | 71124318.2725 | 48892584.5643 | 25215788.1651 | 0
Depreciation (5-Yr Straight Line) | 0 | 27900000 | 27900000 | 27900000 | 27900000 | 27900000
GIDLR Deductible Interest | 0 | 7254000 | 5979947.0643 | 4623080.6877 | 3178017.9967 | 1639026.2307
Taxable Income | 0 | 25601550.3219 | 36444944.264 | 39058212.8671 | 41852565.93 | 44839938.2146
UAE Corporate Tax | 0 | 2304139.529 | 3280044.9838 | 3515239.158 | 3766730.9337 | 4035594.4393
Residual Value Recovery | 0 | 0 | 0 | 0 | 0 | 13950000
Leveraged Free Cash Flow (FCFE) | -27900000 | 31596596.397 | 40190031.9487 | 41211240.0009 | 42309038.5971 | 57438555.6101
Cumulative FCFE | -27900000 | 3696596.397 | 43886628.3457 | 85097868.3466 | 127406906.9437 | 184845462.5538
Debt Service Coverage Ratio (DSCR) | 0 | 2.2624 | 2.6187 | 2.6655 | 2.7157 | 2.7697
Unlevered Tax (no interest shield) | 0 | 2956999.529 | 3818240.2195 | 3931316.4199 | 4052752.5534 | 4183106.8001
Unlevered Free Cash Flow (FCFF) | -139500000 | 57798550.7929 | 66506651.1087 | 67649977.1349 | 68877831.3733 | 84145857.6452
Equity Returns Summary
Equity IRR (5-Yr, levered) | 126.5%
Project IRR (5-Yr, unlevered) | 37.55%
Equity NPV @ hurdle rate | 109809242.3148
MOIC (total distributions / equity) | 7.6253
Payback Period | 0.88301
Minimum DSCR | 2.2624
Average DSCR | 2.6064

## Unit Economics & KPIs
Unit Economics & Operational KPIs
GPU-hour and token-level economics (steady-state Year 2, post-ramp) — all cells formula-driven
KPI | Value | Unit | Derivation
Total GPU Count | 2304 | GPUs | Racks x GPUs per rack
Available GPU-hours / yr | 20082124.8 | GPU-hrs | GPUs x 8760h x uptime
Sold GPU-hours / yr | 17069806.08 | GPU-hrs | Available x utilization
Blended Revenue per Sold GPU-hour | 5.0132 | $/GPU-hr | Year 2 gross revenue / sold GPU-hours
Cash OpEx per Sold GPU-hour | 0.8934 | $/GPU-hr | Year 2 total OpEx / sold GPU-hours
EBITDA per Sold GPU-hour | 4.1198 | $/GPU-hr | Revenue minus cash OpEx per GPU-hour
CapEx per GPU | 60546.875 | $/GPU | Total CapEx / GPU count
CapEx per MW of IT Load | 16880445.3049 | $/MW | Total CapEx / total IT MW
Revenue per MW of IT Load | 10355154.8887 | $/MW/yr | Year 2 revenue / total IT MW
Annual Token Capacity (token fleet) | 33.1837 | T tokens/yr | Token-fleet GPUs x tok/s x seconds x utilization x uptime
Implied Realized Price per M Tokens | 0.80687 | $/M tok | Year 2 token revenue / token capacity
Cash Cost per M Tokens | 0.13787 | $/M tok | Token-fleet share of Year 2 OpEx / token capacity
Energy Cost as % of Revenue | 4.729% | % | Year 2 electricity / Year 2 revenue
Breakeven Power Tariff (EBITDA = 0) | 1.1247 | $/kWh | (Year 2 revenue - fixed OpEx) / annual kWh
Min Revenue for 1.00x DSCR | 42104923.0676 | USD/yr | Debt service + Year 2 OpEx
Revenue Headroom above 1.00x DSCR | 50.8% | % | 1 - min revenue / Year 2 revenue

## Sensitivity Engine
Sensitivity Engine — 16 Live Scenarios
Each row re-runs the full leveraged model (debt schedule, GIDLR tax cap, residual value) for one tariff x debt-ratio combination
Scenario | Tariff $/kWh | Debt % | Debt $ | Equity $ | Debt Service | Y0 FCFE | Y1 FCFE | Y2 FCFE | Y3 FCFE | Y4 FCFE | Y5 FCFE | Equity IRR | Avg DSCR
$0.04/kWh @ 50% debt | 0.04 | 50% | 69750000 | 69750000 | 16784258.9974 | -69750000 | 42625789.0312 | 51286293.0641 | 52377845.9352 | 53549456.9874 | 68756457.3945 | 64.4% | 4.2522
$0.04/kWh @ 60% debt | 0.04 | 60% | 83700000 | 55800000 | 20141110.7969 | -55800000 | 39350544.7317 | 47996715.6691 | 49073003.7935 | 50228357.8904 | 65418044.6401 | 76.24% | 3.5435
$0.04/kWh @ 70% debt | 0.04 | 70% | 97650000 | 41850000 | 23497962.5964 | -41850000 | 36075300.4322 | 44707138.2741 | 45768161.6517 | 46907258.7934 | 62079631.8857 | 95.06% | 3.0373
$0.04/kWh @ 80% debt | 0.04 | 80% | 111600000 | 27900000 | 26854814.3959 | -27900000 | 32800056.1327 | 41417560.8791 | 42463319.51 | 43586159.6963 | 58741219.1313 | 130.7% | 2.6577
$0.06/kWh @ 50% debt | 0.06 | 50% | 69750000 | 69750000 | 16784258.9974 | -69750000 | 41422329.2955 | 50058764.1337 | 51125766.4262 | 52272335.8882 | 67453793.8733 | 62.56% | 4.1702
$0.06/kWh @ 60% debt | 0.06 | 60% | 83700000 | 55800000 | 20141110.7969 | -55800000 | 38147084.996 | 46769186.7387 | 47820924.2844 | 48951236.7912 | 64115381.1189 | 74.01% | 3.4752
$0.06/kWh @ 70% debt | 0.06 | 70% | 97650000 | 41850000 | 23497962.5964 | -41850000 | 34871840.6965 | 43479609.3437 | 44516082.1427 | 45630137.6941 | 60776968.3645 | 92.19% | 2.9787
$0.06/kWh @ 80% debt | 0.06 | 80% | 111600000 | 27900000 | 26854814.3959 | -27900000 | 31596596.397 | 40190031.9487 | 41211240.0009 | 42309038.5971 | 57438555.6101 | 126.5% | 2.6064
$0.08/kWh @ 50% debt | 0.08 | 50% | 69750000 | 69750000 | 16784258.9974 | -69750000 | 40218869.5598 | 48831235.2033 | 49873686.9172 | 50995214.789 | 66151130.3521 | 60.72% | 4.0882
$0.08/kWh @ 60% debt | 0.08 | 60% | 83700000 | 55800000 | 20141110.7969 | -55800000 | 36943625.2603 | 45541657.8083 | 46568844.7754 | 47674115.692 | 62812717.5977 | 71.78% | 3.4069
$0.08/kWh @ 70% debt | 0.08 | 70% | 97650000 | 41850000 | 23497962.5964 | -41850000 | 33668380.9608 | 42252080.4132 | 43264002.6337 | 44353016.5949 | 59474304.8433 | 89.31% | 2.9202
$0.08/kWh @ 80% debt | 0.08 | 80% | 111600000 | 27900000 | 26854814.3959 | -27900000 | 30393136.6613 | 38962503.0182 | 39959160.4919 | 41031917.4979 | 56135892.0889 | 122.3% | 2.5551
$0.10/kWh @ 50% debt | 0.1 | 50% | 69750000 | 69750000 | 16784258.9974 | -69750000 | 39015409.8241 | 47603706.2729 | 48621607.4081 | 49718093.6898 | 64848466.8309 | 58.88% | 4.0062
$0.10/kWh @ 60% debt | 0.1 | 60% | 83700000 | 55800000 | 20141110.7969 | -55800000 | 35740165.5246 | 44314128.8778 | 45316765.2664 | 46396994.5928 | 61510054.0765 | 69.54% | 3.3385
$0.10/kWh @ 70% debt | 0.1 | 70% | 97650000 | 41850000 | 23497962.5964 | -41850000 | 32464921.2251 | 41024551.4828 | 42011923.1246 | 43075895.4957 | 58171641.3221 | 86.43% | 2.8616
$0.10/kWh @ 80% debt | 0.1 | 80% | 111600000 | 27900000 | 26854814.3959 | -27900000 | 29189676.9256 | 37734974.0878 | 38707080.9829 | 39754796.3987 | 54833228.5677 | 118.2% | 2.5039
Scenario EBITDA Grid (Year 1-5)
Scenario | Y1 EBITDA | Y2 EBITDA | Y3 EBITDA | Y4 EBITDA | Y5 EBITDA
$0.04/kWh @ 50% debt | 62078033.5479 | 71673824.2189 | 72957205.1032 | 74334013.7061 | 75810462.8202
$0.04/kWh @ 60% debt | 62078033.5479 | 71673824.2189 | 72957205.1032 | 74334013.7061 | 75810462.8202
$0.04/kWh @ 70% debt | 62078033.5479 | 71673824.2189 | 72957205.1032 | 74334013.7061 | 75810462.8202
$0.04/kWh @ 80% debt | 62078033.5479 | 71673824.2189 | 72957205.1032 | 74334013.7061 | 75810462.8202
$0.06/kWh @ 50% debt | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
$0.06/kWh @ 60% debt | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
$0.06/kWh @ 70% debt | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
$0.06/kWh @ 80% debt | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
$0.08/kWh @ 50% debt | 59433067.0958 | 68975958.4377 | 70205382.0065 | 71527154.1474 | 72947466.0704
$0.08/kWh @ 60% debt | 59433067.0958 | 68975958.4377 | 70205382.0065 | 71527154.1474 | 72947466.0704
$0.08/kWh @ 70% debt | 59433067.0958 | 68975958.4377 | 70205382.0065 | 71527154.1474 | 72947466.0704
$0.08/kWh @ 80% debt | 59433067.0958 | 68975958.4377 | 70205382.0065 | 71527154.1474 | 72947466.0704
$0.10/kWh @ 50% debt | 58110583.8698 | 67627025.5472 | 68829470.4581 | 70123724.368 | 71515967.6954
$0.10/kWh @ 60% debt | 58110583.8698 | 67627025.5472 | 68829470.4581 | 70123724.368 | 71515967.6954
$0.10/kWh @ 70% debt | 58110583.8698 | 67627025.5472 | 68829470.4581 | 70123724.368 | 71515967.6954
$0.10/kWh @ 80% debt | 58110583.8698 | 67627025.5472 | 68829470.4581 | 70123724.368 | 71515967.6954

## Sensitivity Matrices
5-Year Leveraged Sensitivity Matrices
Power tariff ($0.04 - $0.10/kWh) vs. debt ratio (50% - 80%) — every cell is a live link to the Sensitivity Engine
Matrix 1: Leveraged 5-Year Equity IRR (%)
Power Tariff ($/kWh) | 50% Debt | 60% Debt | 70% Debt | 80% Debt
$0.04 / kWh | 64.4% | 76.24% | 95.06% | 130.7%
$0.06 / kWh | 62.56% | 74.01% | 92.19% | 126.5%
$0.08 / kWh | 60.72% | 71.78% | 89.31% | 122.3%
$0.10 / kWh | 58.88% | 69.54% | 86.43% | 118.2%
Matrix 2: Average Debt Service Coverage Ratio (DSCR)
Power Tariff ($/kWh) | 50% Debt | 60% Debt | 70% Debt | 80% Debt
$0.04 / kWh | 4.2522 | 3.5435 | 3.0373 | 2.6577
$0.06 / kWh | 4.1702 | 3.4752 | 2.9787 | 2.6064
$0.08 / kWh | 4.0882 | 3.4069 | 2.9202 | 2.5551
$0.10 / kWh | 4.0062 | 3.3385 | 2.8616 | 2.5039