## Dashboard
AI Factory Dashboard — 32x Vera Rubin NVL72, Abu Dhabi, UAE
Headline KPIs, all live-linked; edit assumptions on 'Control Panel & Inputs'
KPI | Value | Unit | Source Sheet
Equity IRR (levered) | 0.3483% | % | Pro Forma Financials
Project IRR (unlevered) | 4.74% | % | Pro Forma Financials
Equity NPV @ hurdle rate | -29426161.896 | USD | Pro Forma Financials
MOIC | 1.0155 | x | Pro Forma Financials
Payback Period | 4.9767 | years | Pro Forma Financials
Year 1 Gross Revenue | 75600000 | USD | Pro Forma Financials
Year 1 EBITDA | 60755550.3219 | USD | Pro Forma Financials
Year 1 EBITDA Margin | 80.36% | % | Pro Forma Financials
Minimum DSCR | 0.9622 | x | Pro Forma Financials
Peak MLC vs ASHRAE 90.4 | 0.077832 | (limit 0.260) | Thermal Hydraulics & MLC
MLC Compliance Margin | 70.06% | % | Thermal Hydraulics & MLC
Annual Facility Energy | 66124.1613 | MWh/yr | Thermal Hydraulics & MLC
Annual Carbon Emissions | 25788.4229 | tCO2/yr | Thermal Hydraulics & MLC
Annual Water Consumption | 9918.6242 | m³/yr | Thermal Hydraulics & MLC
Total GPU Count | 2304 | GPUs | Unit Economics & KPIs
CapEx per GPU | 142361.1111 | $/GPU | Unit Economics & KPIs
Blended Revenue per Sold GPU-hour | 5.0132 | $/GPU-hr | Unit Economics & KPIs
Cash Cost per M Tokens | 0.13787 | $/M tok | Unit Economics & KPIs
Energy Cost as % of Revenue | 4.729% | % | Unit Economics & KPIs
Breakeven Power Tariff | 1.1247 | $/kWh | Unit Economics & KPIs
Location / ASHRAE 169 Zone | Abu Dhabi, UAE (zone 1A) |  | Control Panel & Inputs
ASHRAE 90.4 MLC Limit (location) | 0.26 | (design max) | Control Panel & Inputs

## Control Panel & Inputs
NVIDIA Vera Rubin NVL72 AI Factory — Abu Dhabi, UAE
Master Control Panel — edit only the yellow Value cells; every other sheet recalculates from them
Category | Parameter | Value | Unit | Notes / Constraints
Geographic & Climate | Geo_Location | Abu Dhabi, UAE |  | Menu choice — drives ASHRAE zone, 90.4 MLC limit and N=20yr peaks
Geographic & Climate | ASHRAE_Climate_Zone | 1A |  | Derived from location — ASHRAE 169 climate zone
Geographic & Climate | ASHRAE_MLC_Limit | 0.26 |  | Derived from location — ASHRAE 90.4 max design MLC
Geographic & Climate | Peak_Ambient_DryBulb | 50 | °C | Derived from location — ASHRAE N=20yr extreme peak dry-bulb
Geographic & Climate | Coincident_WetBulb | 30 | °C | Derived from location — ASHRAE N=20yr peak wet-bulb
Geographic & Climate | Grid_Carbon_Intensity | 0.39 | kgCO2/kWh | Assumption: Abu Dhabi grid avg (Barakah nuclear + gas + solar mix)
Geographic & Climate | Water_Usage_Effectiveness | 0.15 | L/kWh | Assumption: closed-loop dry coolers, minimal adiabatic assist
Technical Specs | VR_Rack_Count | 32 | racks | Vera Rubin NVL72 compute racks
Technical Specs | VR_Rack_Power_kW | 227 | kW/rack | Compute & scale-up busbar load per VR rack
Technical Specs | VR_Cooling_Type | Liquid | Liquid/Air | S45 direct-to-chip liquid loop
Technical Specs | Network_Rack_Count | 6 | racks | Scale-out network fabric racks
Technical Specs | Network_Rack_Power_kW | 100 | kW/rack | Switching + optics load per network rack
Technical Specs | Network_Cooling_Type | Air | Liquid/Air | Hot-aisle containment air cooling
Technical Specs | Storage_Rack_Count | 10 | racks | NVMe object/block storage racks
Technical Specs | Storage_Rack_Power_kW | 40 | kW/rack | Load per storage rack
Technical Specs | Storage_Cooling_Type | Air | Liquid/Air | Hot-aisle containment air cooling
Technical Specs | GPUs_Per_Rack | 72 | GPUs | NVL72 = 72 Rubin GPUs per VR compute rack
Technical Specs | Liquid_Cooling_Overhead | 5% | kW/kW | Cooling power per kW of liquid-cooled IT (CDU pumps, dry-cooler fans)
Technical Specs | Air_Cooling_Overhead | 28% | kW/kW | Cooling power per kW of air-cooled IT (high-ambient chillers, CRAHs)
Technical Specs | Liquid_Supply_Temp_FWS | 45 | °C | S45 direct-to-chip loop
Technical Specs | Liquid_Return_Temp_FWR | 55 | °C | Facility water return — sets the loop delta-T
Technical Specs | Coolant_Specific_Heat | 3.85 | kJ/kg·K | Assumption: PG25 water/glycol at ~50°C
Technical Specs | Coolant_Density | 1.03 | kg/L | Assumption: PG25 mixture density
Technical Specs | Target_Annualized_PUE | 1.08 |  | Drives facility energy = IT energy x PUE
Technical Specs | Cluster_Utilization | 85% | % | Assumption: avg power/capacity utilization of the fleet
Technical Specs | Uptime_Availability | 99.5% | % | Assumption: contractual availability SLA
Technical Specs | Tokens_Per_GPU_Sec | 1800 | tok/s/GPU | Assumption: blended inference throughput per Rubin GPU
Technical Specs | Token_Fleet_Share | 30% | % | Share of fleet serving the API token market
Financial & Fiscal | Electricity_Tariff | 0.06 | $/kWh | Abu Dhabi industrial rate (Year 1)
Financial & Fiscal | Tariff_Escalation | 2% | %/yr | Assumption: annual power price escalation
Financial & Fiscal | CapEx_Initial | 328000000 | USD | All-in benchmark midpoint: ~$91M facility (at $9.9-12.2M/MW) + 32 VR racks at ~$7.4M each (reported $6.0-8.8M). Set to ~$91M if IT is leased/vendor-financed.
Financial & Fiscal | Residual_Value_Pct | 10% | % | Assumption: pre-tax residual recovery of CapEx at end of Year 5
Financial & Fiscal | Debt_Ratio | 80% | % | User adjustable (50% - 80%)
Financial & Fiscal | Interest_Rate | 6.5% | % | Senior debt facility rate
Financial & Fiscal | Debt_Tenor | 5 | Years | Annual amortization schedule
Financial & Fiscal | Model_Horizon_Years | 5 | Years | Pro forma & sensitivity horizon — STRUCTURAL: regenerate the workbook to change (year columns are created at build time)
Financial & Fiscal | Depreciation_Life_Years | 5 | Years | Straight-line depreciation life for the CapEx
Financial & Fiscal | UAE_Corporate_Tax | 9% | % | Statutory corporate tax rate
Financial & Fiscal | GIDLR_EBITDA_Cap | 30% | % | UAE interest deduction limit — applied via MIN() in the tax calc
Financial & Fiscal | Equity_Discount_Rate | 15% | % | Assumption: hurdle rate for equity NPV
Financial & Fiscal | Fixed_OpEx_Annual | 10877000 | USD/yr | Staff, maintenance, insurance, connectivity (Year 1)
Financial & Fiscal | OpEx_Escalation | 3% | %/yr | Assumption: annual fixed-OpEx inflation
Revenue Strategy | Lease_Revenue_70pct | 58800000 | USD/yr | 70% bare-metal capacity leases (Year 1, pre-ramp)
Revenue Strategy | Token_Revenue_30pct | 25200000 | USD/yr | 30% dynamic API token market (Year 1, pre-ramp)
Revenue Strategy | Year1_Ramp_Factor | 90% | % | Assumption: Year 1 commissioning / fill-up ramp
Revenue Strategy | Lease_Price_Escalation | 0% | %/yr | Assumption: lease repricing per year
Revenue Strategy | Token_Price_Decline | 15% | %/yr | Core tokenomics: $/token deflation per year
Revenue Strategy | Token_Volume_Growth | 25% | %/yr | Token demand growth (partially offsets price decline)
Phased Expansion | Expansion_Blocks_Per_Year | 2,2,4,4,4 | blocks/yr | Comma-separated blocks added per year (padded/truncated to the horizon); one block = this workbook's full rack architecture. Live numeric cells are on the 'Phased Expansion' sheet.
Legend: yellow cells with blue text are the editable inputs; all other cells in this workbook are formulas.
Rows marked 'Assumption' are user-supplied estimates, not sourced market data — revisit before investment use.
Geo_Location must exactly match a row on the 'ASHRAE Climate Library' sheet; the four 'Derived from location' rows update automatically. Cooling types must be 'Liquid' or 'Air'.

## ASHRAE Climate Library
ASHRAE Climate & 90.4 Compliance Library
Editable reference data — verify MLC limits against ASHRAE 90.4-2019 Table 6.5.1.1 and temperatures against ASHRAE Fundamentals n=20yr return-period extremes before design use
Location | ASHRAE 169 Zone | ASHRAE 90.4 Max Design MLC | N=20yr Peak Dry-Bulb (°C) | N=20yr Peak Wet-Bulb (°C) | Notes
Abu Dhabi, UAE | 1A | 0.26 | 50 | 30 | Project baseline; ASHRAE 169-2021 may reclassify as 0B
Dubai, UAE | 0B | 0.28 | 49.5 | 31
Riyadh, Saudi Arabia | 0B | 0.28 | 49 | 24 | Dry extreme heat
Singapore | 0A | 0.28 | 36.5 | 29.5 | High wet-bulb year-round
Mumbai, India | 0A | 0.28 | 39.5 | 30
Phoenix, AZ, USA | 2B | 0.25 | 48.5 | 26.5
Dallas, TX, USA | 3A | 0.21 | 43.5 | 27.5
Ashburn, VA, USA | 4A | 0.19 | 39 | 27 | N. Virginia hub
Chicago, IL, USA | 5A | 0.16 | 38.5 | 27
Frankfurt, Germany | 5A | 0.16 | 37.5 | 23
Amsterdam, Netherlands | 5A | 0.16 | 35 | 22
Dublin, Ireland | 5A | 0.16 | 28.5 | 19.5 | Free-cooling friendly
Oslo, Norway | 6A | 0.15 | 32 | 21
Tokyo, Japan | 3A | 0.21 | 37.5 | 27.5
Sydney, Australia | 3A | 0.21 | 43 | 24.5

## Thermal Hydraulics & MLC
Thermal Hydraulics & ASHRAE 90.4 Compliance Engine
S45 closed-loop fluid dynamics, 3-stage trim cooling, and annual energy / water / carbon footprint
Metric / Calculation Step | Value | Unit | Notes
VR Compute Rack Load | 7264 | kW | VR racks x kW/rack
Network Rack Load | 600 | kW | Network racks x kW/rack
Storage Rack Load | 400 | kW | Storage racks x kW/rack
Total Combined IT Load | 8264 | kW | VR compute + network + storage
Liquid-Cooled IT Load | 7264 | kW | Sum of rack classes whose cooling type is 'Liquid'
Air-Cooled IT Load | 1000 | kW | Total IT load minus liquid-cooled load
Liquid-Cooled Rack Count | 32 | racks | Racks on the S45 loop (cooling type = 'Liquid')
S45 Loop Supply Temperature | 45 | °C | Facility Water Supply (FWS)
S45 Loop Return Temperature | 55 | °C | Facility Water Return (FWR)
S45 Loop Delta T | 10 | °C | Hydraulic temperature split
S45 Liquid Flow Rate per VR Rack | 343.4624 | LPM | Physics: Q/(rho*Cp*dT)*60 — flow required to absorb one VR rack
Total S45 Cluster Flow Rate | 10990.7956 | LPM | Physics: liquid-cooled load/(rho*Cp*dT)*60
Peak Ambient Dry-Bulb (N=20yr) | 50 | °C | ASHRAE n=20yr extreme — derived from location
Peak Wet-Bulb (N=20yr) | 30 | °C | ASHRAE n=20yr — derived from location
S45 Peak Rejection Approach | 5 | K | FWR minus peak dry-bulb (positive = dry cooling viable)
Liquid Loop Cooling Power | 363.2 | kW | Liquid-cooled load x liquid cooling overhead input
Air Loop Cooling Power | 280 | kW | Air-cooled load x air cooling overhead input
Total Cooling Peak Power | 643.2 | kW | Combined cooling power
Peak Mechanical Load Component (MLC) | 0.077832 |  | Cooling power / total IT load
ASHRAE 90.4 MLC Limit (from location) | 0.26 |  | Max design MLC for the selected location's climate zone
Safety Compliance Margin | 70.06% | % | Operational margin under the location's 90.4 limit
Average Utilized IT Power | 6989.278 | kW | Total IT x utilization x uptime
Annualized PUE | 1.08 |  | Facility energy multiplier on IT energy
Annual Facility Energy | 66124.1613 | MWh/yr | Avg IT power x 8760h x PUE
Annual Water Consumption | 9918.6242 | m³/yr | Facility kWh x WUE
Annual Carbon Emissions | 25788.4229 | tCO2/yr | Facility kWh x grid intensity

## Pro Forma Financials
5-Year Leveraged Financial Model & Debt Amortization
UAE corporate tax (9%) with GIDLR 30%-of-EBITDA interest cap, revenue ramp & escalations, full debt schedule and equity returns
Line Item (USD) | Year 0 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5
Revenue Ramp Factor | 0% | 90% | 100% | 100% | 100% | 100%
Lease Revenue | 0 | 52920000 | 58800000 | 58800000 | 58800000 | 58800000
Token Revenue | 0 | 22680000 | 26775000 | 28448437.5 | 30226464.8438 | 32115618.8965
Gross Annual Revenue | 0 | 75600000 | 85575000 | 87248437.5 | 89026464.8438 | 90915618.8965
Effective Power Tariff | 0 | 0.06 | 0.0612 | 0.062424 | 0.063672 | 0.064946
Annual Facility Energy (kWh) | 0 | 66124161.3024 | 66124161.3024 | 66124161.3024 | 66124161.3024 | 66124161.3024
Electricity Cost | 0 | 3967449.6781 | 4046798.6717 | 4127734.6451 | 4210289.338 | 4294495.1248
Fixed Non-Power OpEx | 0 | 10877000 | 11203310 | 11539409.3 | 11885591.579 | 12242159.3264
Total Operational Expense (OpEx) | 0 | 14844449.6781 | 15250108.6717 | 15667143.9451 | 16095880.917 | 16536654.4512
EBITDA | 0 | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
EBITDA Margin | 0% | 80.36% | 82.18% | 82.04% | 81.92% | 81.81%
CapEx Initial Outlay | 328000000 | 0 | 0 | 0 | 0 | 0
Debt Financed Amount | 262400000 | 0 | 0 | 0 | 0 | 0
Equity Outlay | 65600000 | 0 | 0 | 0 | 0 | 0
Beginning Debt Balance | 0 | 262400000 | 216313497.3344 | 167231371.9956 | 114958908.5097 | 59288734.8973
Annual Debt Service (P+I) | 0 | 63142502.6656 | 63142502.6656 | 63142502.6656 | 63142502.6656 | 63142502.6656
Interest Expense | 0 | 17056000 | 14060377.3267 | 10870039.1797 | 7472329.0531 | 3853767.7683
Debt Principal Payment | 0 | 46086502.6656 | 49082125.3388 | 52272463.4859 | 55670173.6124 | 59288734.8973
Ending Debt Balance | 0 | 216313497.3344 | 167231371.9956 | 114958908.5097 | 59288734.8973 | 0
Depreciation (Straight Line) | 0 | 65600000 | 65600000 | 65600000 | 65600000 | 65600000
GIDLR Deductible Interest | 0 | 17056000 | 14060377.3267 | 10870039.1797 | 7472329.0531 | 3853767.7683
Taxable Income | 0 | -21900449.6781 | -9335485.9984 | -4888745.6249 | -141745.1264 | 4925196.677
UAE Corporate Tax | 0 | 0 | 0 | 0 | 0 | 443267.7009
Residual Value Recovery | 0 | 0 | 0 | 0 | 0 | 32800000
Leveraged Free Cash Flow (FCFE) | -65600000 | -2386952.3437 | 7182388.6627 | 8438790.8893 | 9788081.2611 | 43593194.0788
Cumulative FCFE | -65600000 | -67986952.3437 | -60804563.681 | -52365772.7917 | -42577691.5306 | 1015502.5482
Debt Service Coverage Ratio (DSCR) | 0 | 0.9622 | 1.1137 | 1.1336 | 1.155 | 1.178
Unlevered Tax (no interest shield) | 0 | 0 | 425240.2195 | 538316.4199 | 659752.5534 | 790106.8001
Unlevered Free Cash Flow (FCFF) | -328000000 | 60755550.3219 | 69899651.1087 | 71042977.1349 | 72270831.3733 | 106388857.6452
Equity Returns Summary
Equity IRR (levered) | 0.3483%
Project IRR (unlevered) | 4.74%
Equity NPV @ hurdle rate | -29426161.896
MOIC (total distributions / equity) | 1.0155
Payback Period | 4.9767
Minimum DSCR | 0.9622
Average DSCR | 1.1085

## Unit Economics & KPIs
Unit Economics & Operational KPIs
GPU-hour and token-level economics (steady-state Year 2, post-ramp) — all cells formula-driven
KPI | Value | Unit | Derivation
Total GPU Count | 2304 | GPUs | Racks x GPUs per rack
Available GPU-hours / yr | 20082124.8 | GPU-hrs | GPUs x 8760h x uptime
Sold GPU-hours / yr | 17069806.08 | GPU-hrs | Available x utilization
Blended Revenue per Sold GPU-hour | 5.0132 | $/GPU-hr | Year 2 gross revenue / sold GPU-hours
Cash OpEx per Sold GPU-hour | 0.8934 | $/GPU-hr | Year 2 total OpEx / sold GPU-hours
EBITDA per Sold GPU-hour | 4.1198 | $/GPU-hr | Revenue minus cash OpEx per GPU-hour
CapEx per GPU | 142361.1111 | $/GPU | Total CapEx / GPU count
CapEx per MW of IT Load | 39690222.6525 | $/MW | Total CapEx / total IT MW
Revenue per MW of IT Load | 10355154.8887 | $/MW/yr | Year 2 revenue / total IT MW
Annual Token Capacity (token fleet) | 33.1837 | T tokens/yr | Token-fleet GPUs x tok/s x seconds x utilization x uptime
Implied Realized Price per M Tokens | 0.80687 | $/M tok | Year 2 token revenue / token capacity
Cash Cost per M Tokens | 0.13787 | $/M tok | Token-fleet share of Year 2 OpEx / token capacity
Energy Cost as % of Revenue | 4.729% | % | Year 2 electricity / Year 2 revenue
Breakeven Power Tariff (EBITDA = 0) | 1.1247 | $/kWh | (Year 2 revenue - fixed OpEx) / annual kWh
Min Revenue for 1.00x DSCR | 78392611.3373 | USD/yr | Debt service + Year 2 OpEx
Revenue Headroom above 1.00x DSCR | 8.393% | % | 1 - min revenue / Year 2 revenue

## Sensitivity Engine
Sensitivity Engine — 16 Live Scenarios over 5 Years
Each row re-runs the full leveraged model (debt schedule, GIDLR tax cap, residual value) for one tariff x debt-ratio combination
Scenario | Tariff $/kWh | Debt % | Debt $ | Equity $ | Debt Service | Y0 FCFE | Y1 FCFE | Y2 FCFE | Y3 FCFE | Y4 FCFE | Y5 FCFE | Equity IRR | Avg DSCR
$0.04/kWh @ 50% debt | 0.04 | 50% | 164000000 | 164000000 | 39464064.166 | -164000000 | 22613969.3819 | 32209760.0529 | 33442432.1818 | 34504206.8158 | 68444231.4374 | 4.556% | 1.8085
$0.04/kWh @ 60% debt | 0.04 | 60% | 196800000 | 131200000 | 47356876.9992 | -131200000 | 14721156.5487 | 24316947.2197 | 25600328.1041 | 26695457.6844 | 60594773.4916 | 4.183% | 1.5071
$0.04/kWh @ 70% debt | 0.04 | 70% | 229600000 | 98400000 | 55249689.8324 | -98400000 | 6828343.7155 | 16424134.3865 | 17707515.2709 | 18886708.5531 | 52745315.5458 | 3.603% | 1.2918
$0.04/kWh @ 80% debt | 0.04 | 80% | 262400000 | 65600000 | 63142502.6656 | -65600000 | -1064469.1177 | 8531321.5533 | 9814702.4377 | 11077959.4217 | 44895857.6 | 2.615% | 1.1303
$0.06/kWh @ 50% debt | 0.06 | 50% | 164000000 | 164000000 | 39464064.166 | -164000000 | 21291486.1559 | 30860827.1623 | 32117229.3889 | 33227085.7166 | 67141567.9162 | 3.47% | 1.7736
$0.06/kWh @ 60% debt | 0.06 | 60% | 196800000 | 131200000 | 47356876.9992 | -131200000 | 13398673.3227 | 22968014.3291 | 24224416.5557 | 25418336.5852 | 59292109.9704 | 2.859% | 1.478
$0.06/kWh @ 70% debt | 0.06 | 70% | 229600000 | 98400000 | 55249689.8324 | -98400000 | 5505860.4895 | 15075201.4959 | 16331603.7225 | 17609587.4539 | 51442652.0246 | 1.93% | 1.2669
$0.06/kWh @ 80% debt | 0.06 | 80% | 262400000 | 65600000 | 63142502.6656 | -65600000 | -2386952.3437 | 7182388.6627 | 8438790.8893 | 9788081.2611 | 43593194.0788 | 0.3483% | 1.1085
$0.08/kWh @ 50% debt | 0.08 | 50% | 164000000 | 164000000 | 39464064.166 | -164000000 | 19969002.9298 | 29511894.2717 | 30741317.8405 | 31949964.6173 | 65838904.395 | 2.366% | 1.7387
$0.08/kWh @ 60% debt | 0.08 | 60% | 196800000 | 131200000 | 47356876.9992 | -131200000 | 12076190.0966 | 21619081.4385 | 22848505.0073 | 24141215.486 | 57989446.4492 | 1.523% | 1.449
$0.08/kWh @ 70% debt | 0.08 | 70% | 229600000 | 98400000 | 55249689.8324 | -98400000 | 4183377.2634 | 13726268.6053 | 14955692.1741 | 16277464.315 | 50139988.5034 | 0.2264% | 1.242
$0.08/kWh @ 80% debt | 0.08 | 80% | 262400000 | 65600000 | 63142502.6656 | -65600000 | -3709435.5698 | 5833455.7721 | 7062879.3409 | 8384651.4818 | 42290530.5576 | -1.978% | 1.0867
$0.10/kWh @ 50% debt | 0.1 | 50% | 164000000 | 164000000 | 39464064.166 | -164000000 | 18646519.7038 | 28162961.3812 | 29365406.2921 | 30659660.202 | 64536240.8738 | 1.25% | 1.7039
$0.10/kWh @ 60% debt | 0.1 | 60% | 196800000 | 131200000 | 47356876.9992 | -131200000 | 10753706.8706 | 20270148.548 | 21472593.4589 | 22766847.3688 | 56686782.928 | 0.1536% | 1.4199
$0.10/kWh @ 70% debt | 0.1 | 70% | 229600000 | 98400000 | 55249689.8324 | -98400000 | 2860894.0374 | 12377335.7148 | 13579780.6257 | 14874034.5356 | 48837324.9822 | -1.514% | 1.217
$0.10/kWh @ 80% debt | 0.1 | 80% | 262400000 | 65600000 | 63142502.6656 | -65600000 | -5031918.7958 | 4484522.8816 | 5686967.7925 | 6981221.7024 | 40987867.0364 | -4.327% | 1.0649
Scenario EBITDA Grid (Year 1-5)
Scenario | Y1 EBITDA | Y2 EBITDA | Y3 EBITDA | Y4 EBITDA | Y5 EBITDA
$0.04/kWh @ 50% debt | 62078033.5479 | 71673824.2189 | 72957205.1032 | 74334013.7061 | 75810462.8202
$0.04/kWh @ 60% debt | 62078033.5479 | 71673824.2189 | 72957205.1032 | 74334013.7061 | 75810462.8202
$0.04/kWh @ 70% debt | 62078033.5479 | 71673824.2189 | 72957205.1032 | 74334013.7061 | 75810462.8202
$0.04/kWh @ 80% debt | 62078033.5479 | 71673824.2189 | 72957205.1032 | 74334013.7061 | 75810462.8202
$0.06/kWh @ 50% debt | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
$0.06/kWh @ 60% debt | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
$0.06/kWh @ 70% debt | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
$0.06/kWh @ 80% debt | 60755550.3219 | 70324891.3283 | 71581293.5549 | 72930583.9267 | 74378964.4453
$0.08/kWh @ 50% debt | 59433067.0958 | 68975958.4377 | 70205382.0065 | 71527154.1474 | 72947466.0704
$0.08/kWh @ 60% debt | 59433067.0958 | 68975958.4377 | 70205382.0065 | 71527154.1474 | 72947466.0704
$0.08/kWh @ 70% debt | 59433067.0958 | 68975958.4377 | 70205382.0065 | 71527154.1474 | 72947466.0704
$0.08/kWh @ 80% debt | 59433067.0958 | 68975958.4377 | 70205382.0065 | 71527154.1474 | 72947466.0704
$0.10/kWh @ 50% debt | 58110583.8698 | 67627025.5472 | 68829470.4581 | 70123724.368 | 71515967.6954
$0.10/kWh @ 60% debt | 58110583.8698 | 67627025.5472 | 68829470.4581 | 70123724.368 | 71515967.6954
$0.10/kWh @ 70% debt | 58110583.8698 | 67627025.5472 | 68829470.4581 | 70123724.368 | 71515967.6954
$0.10/kWh @ 80% debt | 58110583.8698 | 67627025.5472 | 68829470.4581 | 70123724.368 | 71515967.6954

## Sensitivity Matrices
5-Year Leveraged Sensitivity Matrices
Power tariff ($0.04 - $0.10/kWh) vs. debt ratio (50% - 80%) — every cell is a live link to the Sensitivity Engine
Matrix 1: Leveraged 5-Year Equity IRR (%)
Power Tariff ($/kWh) | 50% Debt | 60% Debt | 70% Debt | 80% Debt
$0.04 / kWh | 4.556% | 4.183% | 3.603% | 2.615%
$0.06 / kWh | 3.47% | 2.859% | 1.93% | 0.3483%
$0.08 / kWh | 2.366% | 1.523% | 0.2264% | -1.978%
$0.10 / kWh | 1.25% | 0.1536% | -1.514% | -4.327%
Matrix 2: Average Debt Service Coverage Ratio (DSCR)
Power Tariff ($/kWh) | 50% Debt | 60% Debt | 70% Debt | 80% Debt
$0.04 / kWh | 1.8085 | 1.5071 | 1.2918 | 1.1303
$0.06 / kWh | 1.7736 | 1.478 | 1.2669 | 1.1085
$0.08 / kWh | 1.7387 | 1.449 | 1.242 | 1.0867
$0.10 / kWh | 1.7039 | 1.4199 | 1.217 | 1.0649

## Phased Expansion
Phased Campus Expansion — Identical Blocks
Each block replicates this workbook's rack architecture; block economics use the single-block Year-2 (steady-state) pro forma. Simplification: per-vintage token-price dynamics and per-block financing are not modeled here.
Metric | Year 1 | Year 2 | Year 3 | Year 4 | Year 5
Blocks Added (input) | 2 | 2 | 4 | 4 | 4
Cumulative Blocks | 2 | 4 | 8 | 12 | 16
Campus IT Capacity (MW) | 16.528 | 33.056 | 66.112 | 99.168 | 132.224
Campus GPUs | 4608 | 9216 | 18432 | 27648 | 36864
Effective Revenue Blocks | 1.8 | 3.8 | 7.6 | 11.6 | 15.6
Campus Revenue | 154035000 | 325185000 | 650370000 | 992670000 | 1334970000
Campus EBITDA | 126584804.3909 | 267234587.0475 | 534469174.095 | 815768739.4082 | 1097068304.7214
CapEx Deployed | 656000000 | 656000000 | 1312000000 | 1312000000 | 1312000000
Campus Net Cash Flow | -529415195.6091 | -388765412.9525 | -777530825.905 | -496231260.5918 | -214931695.2786
Cumulative Funding Position | -529415195.6091 | -918180608.5616 | -1695711434.4665 | -2191942695.0583 | -2406874390.337
Campus KPIs
Peak Funding Requirement | -2406874390.337
Campus Cash-Positive Year | >5
Final Campus IT Capacity (MW) | 132.224
Final Campus GPUs | 36864
Run-Rate Campus EBITDA (full blocks) | 1125198261.2527
Total Campus CapEx | 5248000000